{"text_format":"3","workbook":"xls","n_sheets":2,"sheets":["榕山","化验室易耗品（自行采购）"],"not_rendered":{"images":1,"external_links":1,"defined_names":1},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"榕山","index":0,"n_rows":97,"n_cols":10,"rows_kept":97,"merged":[[0,0,0,9],[1,1,1,2],[2,0,5,0],[2,1,5,1],[6,0,13,0],[6,1,13,1],[6,2,13,2],[14,0,25,0],[14,1,25,1],[18,2,21,2],[22,2,25,2],[27,0,28,0],[27,1,28,1],[29,0,31,0],[29,1,31,1],[32,0,33,0],[32,1,33,1],[32,9,33,9],[34,0,45,0],[34,1,45,1],[34,9,45,9],[46,0,51,0],[46,1,51,1],[46,2,50,2],[52,0,53,0],[52,1,53,1],[55,0,61,0],[55,1,61,1],[62,0,84,0],[62,1,84,1],[85,0,94,0],[85,1,93,1],[95,0,95,2],[96,0,96,9]],"flags":["formulas_cached_only"]}
["合江县城镇生活污水环保攻坚项目（临港街道等城市生活污水处理厂）\n询价报价表"]
["序号","名称",null,"要求（型号参数）","数量","单位","品牌","单价","合价","备注"]
[1,"风机房","磁悬浮离心式鼓风机","成套自控及安装，包括涡街流量计。厂区采用AAO工艺要求，单机须满足生化池容积1800m³，有效水深大于6m的使用要求。",2,"台","推荐品牌：南京磁谷、天津亿昇、山东天瑞重工"]
[null,null,"配套风管","D219不锈钢管",40,"米","——",null,null,"包含D219不锈钢主风管约40米，相应配套管配件及、支架。新建风机房到AAO生化池D219不锈钢管道约40米连通曝气主管。（含放空阀、配套法兰、弯头等配件）"]
[null,null,"配套动力电缆","4*70+1*35（国标）",50,"米","——"]
[null,null,"电动葫芦","起重量大于2吨-3吨，起吊高度5.0m，功率3KW。L*B*H=7.7*6.8*7.1m。双轨",1,"台","推荐品牌：河南豫重、河南卫华、河南矿山",null,null,"含一根22a工字钢轨道约15米，以房间具体尺寸为准。"]
[2,"生化池","AAO曝气池系统改造","曝气盘：陶瓷微孔刚玉曝气器。\n材质：刚玉+ABS，φ178mm。\n水池尺寸：L*B*H=28*15.4*5.7m。",1050,"个","推荐品牌：江苏天马、河南新浪、宜兴奇美",null,null,"以曝气盘以上1M为界，以下为设备成套供应。曝气盘以下1M为界，曝气系统全部拆除，好氧池清理。"]
[{"$nulls":3},"泄水清污装置系统，大小DN20，材质化工级UPVC",1,"套","——",null,null,"约120米，以曝气系统轴测图及安装大样图。多套"]
[{"$nulls":3},"涡轮式手动蝶阀DN100；PN1.0MPa；材质SS304。",12,"个","国产知名品牌",null,null,"阀体：聚四氟；碟板：不锈钢；密封圈：不锈钢；阀杆：不锈钢"]
[{"$nulls":3},"PH在线检测仪，PH6.3控制器，通讯，黑色，中文，220V供电，PH复合电极（5019），5米，温补（NTC10K），耐温0-60度，带安装支架；",6,"套","推荐品牌：哈希、美仪、川仪",null,null,"成套设备含仪表操作箱等；各类仪器分别注明品牌和单价"]
[{"$nulls":3},"ORP在线检测仪，ORP6.3控制器，通讯，黑色，中文，220V供电，ORP电极（6040），5米，耐温0-60度，带安装支架；",4,"套","推荐品牌：哈希、美仪、川仪",null,null,"成套设备含仪表操作箱等；各类仪器分别注明品牌和单价"]
[{"$nulls":3},"溶解氧在线检测仪,控制器：220VAC供电，4-20mA输出，RS485输出，LED中文显示，配国产膜头，量程：溶解氧：0-20 mg/L、0-20 ppm，温度：0-45℃；精度：溶解氧：测量值±3%，温度：±0.5℃；标配电缆长度：10米，配支架；",6,"套","推荐品牌：哈希、美仪、川仪",null,null,"成套设备含仪表操作箱等；各类仪器分别注明品牌和单价"]
[{"$nulls":3},"MLSS：量程0-20g/L，4-20mA输出，继电器输出，485通讯，220V供电，10米线缆，沉入式探头，自动清洗装置，2米沉入式安装；",2,"套","推荐品牌：哈希、美仪、川仪",null,null,"成套设备含仪表操作箱等；各类仪器分别注明品牌和单价"]
[{"$nulls":3},"超声波液位计：量程大于8m，防水。",2,"套","推荐品牌：哈希、美仪、川仪",null,null,"1.成套设备含仪表操作箱等；各类仪器分别注明品牌和单价\n2.PH和ORP可以为一体或分体"]
[3,"生化池","调节池-搅拌机","QJB4/6-400/3-980/S， 功率3KW ，桨叶直径400mm，转 速980rmp.，与水下接触部分均为不锈钢，配套起吊支架ss304，带转向功能。水池L*B*H=14.5*13.2*7.5m。",3,"台","推荐品牌：蓝深、南京蓝奥、上海南蓝"]
[null,null,"接触氧化池（组合）-潜水搅拌机","QJB0.85/8-260/3-980/S， 功率0.85KW ，桨叶直径 260mm，转速980rmp.与水下接触部分均为不锈钢，配套起吊支架ss304，带转向功能。水池L*B*H=5*2.5*5.5m。",3,"台","推荐品牌：蓝深、南京蓝奥、上海南蓝"]
[null,null,"接触氧化池（组合）-好氧池填料","聚丙烯弹性纤维填料，填料高度3.0m，安装间距150-180mm",550,"m³","国产知名品牌",null,null,"以曝气盘以上1M为界，以下为设备成套供应。曝气盘以下1M为界，曝气系统全部拆除，好氧池清理。"]
[null,null,"接触氧化池（组合）-可变微孔管式曝气器","de85L-1800mm,水池L*B*H=10.4*9.6*5.5m。DN20泄水清污阀管道，材质化工级UPVC约30米。数量：100个",1,"套","国产知名品牌",null,null,"以曝气盘以上1M为界，以下为设备成套供应。曝气盘以下1M为界，曝气系统全部拆除，好氧池清理。"]
[null,null,"阀门管件","DN100配套不锈钢法兰",4,"个","国产知名品牌"]
[{"$nulls":3},"DN100 、PN1.0MPa涡轮式手动蝶阀，材质SS",12,"个","国产知名品牌"]
[{"$nulls":3},"DN150、PN1.0MPa涡轮式手动蝶阀；材质SS",2,"个","国产知名品牌"]
[{"$nulls":3},"DN100配套不锈钢法兰",24,"个","国产知名品牌"]
[null,null,"仪表","PH在线检测仪，PH6.3控制器，通讯，中文，220V供电，PH复合电极（5019），5米，温补（NTC10K），耐温0-60度，带安装支架",4,"套","推荐品牌：哈希、美仪、川仪"]
[{"$nulls":3},"ORP在线检测仪，ORP6.3控制器，通讯，黑色，中文，220V供电，ORP电极（6040），5米，耐温0-60度，带安装支架；",4,"套","推荐品牌：哈希、美仪、川仪"]
[{"$nulls":3},"溶解氧在线检测仪,控制器：220VAC供电，4-20mA输出，RS485输出，LED中文显示，配国产膜头，量程：溶解氧：0-20 mg/L、0-20 ppm，温度：0-45℃；精度：溶解氧：测量值±3%，温度：±0.5℃；标配电缆长度：10米，配支架；",4,"套","推荐品牌：哈希、美仪、川仪"]
[{"$nulls":3},"MLSS，量程0-20g/L，4-20mA输出，继电器输出，485通讯，220V供电，10米线缆，沉入式探头，自动清洗装置，2米沉入式安装；",4,"套","推荐品牌：哈希、美仪、川仪",null,null,"成套设备含仪表操作箱等\n各类仪器分别注明品牌和单价"]
[4,"生物转盘","生物转盘过滤器","处理量40-50L/s，滤盘直径2m,（主要配件参数：冲洗水泵Q=50m³/h，H=7m，N=2.2KW，2台；电动球阀DN80,Pe=0.04KW；弹性接头DN65,8个；进水可调堰板L*B=2000*400mm，2块；出水可调堰板L*B=2600*400m，2块）",2,"套","推荐品牌：江苏天雨、江苏宜兴新纪元、江苏格立",null,null,"1.厂家需提供成套设备需要的辅助设备、自控仪表及其他附件，以工艺设计图纸为准，满足工艺要求和使用功能。\n2.满足每组3000m³/d的过水，含所有配套设施接入中控。"]
[5,"泵站","泵站细格栅机","B=1.2m，H=5.5m，ɑ=75°，栅隙3mm，SS304材质。",1,"套","推荐品牌：扬州天朗、江苏格立、江苏峰科"]
[null,null,"启闭机","DN600、H=6m",1,"套","——",null,null,"手自一体；含丝杆总成、阀门等配件"]
[6,"脱泥设备","叠螺脱水机","处理能力大于20m³/h，Q=1145kgDS/d。含PAC\\PAM加药计量系统与污泥处理电磁流量计等配套装置。",2,"套","推荐品牌：上海同臣、上海凌盛、安尼康",null,null,"配套脱泥PAC加药系统两套（含加药桶4m³2个、计量泵2台，UPVC管道系统、电控系统）"]
[null,null,"污泥切割机","Q=20-50m³/h  N=2.2KW",2,"套","推荐品牌：上海寰一、耐驰、西派克",null,null,"和污泥螺杆泵配套供货（含相应的管道、阀门软连接等，以污泥脱水机管道系统图为准）"]
[null,null,"污泥螺杆泵","Q=20-50m³/h   P=0.3MPa   N=2.2KW",3,"套","推荐品牌：上海寰一、耐驰、西派克",null,null,"和污泥切割机配套供货（含相应的管道、阀门软连接等，以污泥脱水机管道系统图为准）"]
[7,"沉砂池","钟式除砂器","∅=2130,处理量360m³/h N=1.1KW",2,"套","推荐品牌：江苏天雨、无锡通用、江苏格立",null,null,"1.配套就地控制柜、电磁阀和管道，满足独立系统控制，预留PLC接入点位。满足除砂系统单元工艺要求和使用功能。\n2.由供货方整改处理后满足使用功能，对风机进行更换。"]
[null,null,"鼓风机","Q=2m³/min,P=39.2kPa,N=2.2KW",2,"套","推荐品牌：百事德、章丘三叶、川源"]
[8,"实验室","多参数测定仪","同时满足测量DO、pH、ORP、T（含可携带工具箱）",1,"套","推荐品牌：雷磁",null,null,"供货设置应满足化验设备参数（详细参数见附件），含安装与人员培训。"]
[null,null,"红外测油仪","油类（不含萃取仪）",1,"套","推荐品牌：陕西明澈"]
[null,null,"离心机","转速可调，5000转每分钟以上，容量6x100ml",1,"套","——"]
[null,null,"程控定量封口机","定量检测盘/定量孔板 ，97孔",1,"套","推荐品牌：西安立科"]
[null,null,"陶瓷纤维马弗炉","使用温度范围：100-1200℃；温度控制精度：±1℃；内容积：7L",1,"套","推荐品牌：天津泰斯特"]
[null,null,"生化培养箱","1.2KW;22层；250L",1,"套","推荐品牌：天津泰斯特"]
[null,null,"电热恒温培养箱","使用温度范围：5-80℃；温度分布精度：±1℃；内容积：65L",1,"套","推荐品牌：天津泰斯特"]
[null,null,"电热恒温水浴锅","双列八孔；使用温度范围：5-100℃；温度分布精度：±1℃；内容积：24.8L；\n额定功率：2kW",1,"套","推荐品牌：天津泰斯特"]
[null,null,"紫外分光光度计（自动计算测TN）","0.5, 1, 2, 4,5nm五档可调",1,"套","推荐品牌：屹谱仪器"]
[null,null,"真空泵及配套抽滤装置","双抽头，全玻璃微孔抽滤器，布氏漏斗抽滤器",1,"套","推荐品牌：巩义科瑞仪器"]
[null,null,"JQ-1000S型自动液萃取仪","1×6个样品 标配6个500ml萃取瓶（加6个1000ML）；7寸彩色触摸屏",1,"套","推荐品牌：菁工仪器"]
[null,null,"生物化学需氧量（BOD5）测定仪","每个测试单元独立，可灵活决定当个样品开始时间。",1,"套","推荐品牌：连华"]
[9,"辅材","潜污泵","100WQ60-10-4",15,"台","推荐品牌：南方、新界、连成、上海进亨"]
[{"$nulls":3},"100WQ65-18-5.5",10,"台","推荐品牌：南方、新界、连成"]
[{"$nulls":3},"80WQ40-10-3",4,"台","推荐品牌：南方、新界、连成"]
[{"$nulls":3},"50WQ15-12-2.2",12,"台","推荐品牌：南方、新界、连成"]
[{"$nulls":3},"65WQ25-12-3",20,"台","推荐品牌：南方、新界、连成"]
[null,null,"潜水搅拌机","QJB1.5/6-260/3-980/S， 功率1.5KW ，桨叶直径260mm， 转速980rmp.",19,"套","推荐品牌：蓝深、上海南蓝、南京蓝奥",null,null,"导轨卡槽5cm—17台，导轨卡槽6cm—2台；\n配套4套5cm导轨。"]
[10,"安全设备","浸水防触电保护器","规格：183MM*198MM*336MM\n最大输出电流：400A\n额定电压：380V\n最大负载：约210.6Kw\n接续方式：串联\n安装方式：挂壁式",1,"套","推荐品牌：维克安"]
[null,null,"浸水防触电保护器","规格：138MM*122MM*220MM\n最大输出电流：125A\n额定电压：380V\n最大负载：约65.8Kw\n接续方式：串联\n安装方式：挂壁式",23,"套","推荐品牌：维克安"]
[11,"膜池","MBR膜丝","1、设计瞬时产水通量：13LMH。\n2、设计运行时间18h，MBR膜运行方式开8停2。\n3、膜组件设计： \n膜元件选择20㎡/帘，尺寸：2010*535*45mm\n膜元件132帘，膜组件3组，每组44帘膜元件共2640㎡。\n膜组件尺寸2400*1410*2400mm，膜间距100mm。",2640,"平方米","推荐品牌：海普润、膜天、净泽",null,null,"成套设备，含配件"]
[12,"生化池","污水污物泵","WQ65-15-5.5L","台",2,"推荐品牌：新界、南方、蓝深、上海进亨",null,null,"配管内径102mm，流量65m3/h，扬程15米，功率5.5kw。配304不锈钢起吊装置。回流到厌氧池。"]
[null,null,"污水污物泵","WQ40-15-4L","台",2,"推荐品牌：新界、南方、蓝深、上海进亨",null,null,"口径76mm，流量40m3/h，扬程15米，功率4kw。配304不锈钢起吊装置。"]
[null,null,"PE管材","110mm","米",60]
[null,null,"污水污物泵","WQ65-15-5.5L；配管内径102mm，流量65m3/h，扬程15米，功率5.5kw。","台",2,"推荐品牌：新界、南方、蓝深、上海进亨"]
[null,null,"PE管材","110mm","米",80,{"$nulls":3},"配110三通1个，110-90三通1个，直接头弯头各8个。90球阀，弯头各2个。110球阀2个"]
[null,null,"管道","dn50；PE材质","米",35]
[null,null,"污水污物泵","50WQ-2.2CS","台",1,"推荐品牌：新界、南方、蓝深、上海进亨",null,null,"全不锈钢材质，带切割功能。口径50，流量15m³/h，扬程20m，功率2.2kw"]
[13,"PLC","壳体","2200*800*600；碳钢","台",1]
[null,null,"断路器","3P 160A","块",1,"推荐品牌：正泰"]
[null,null,"断路器","3P D25","块",16,"推荐品牌：正泰"]
[null,null,"断路器","3P D10","块",6,"推荐品牌：正泰"]
[null,null,"断路器（含仪表供电）","1P C6","块",15,"推荐品牌：正泰"]
[null,null,"ET200M","153-1AA03","台",1,"推荐品牌：西门子"]
[null,null,"32DI模块","321-1BL00","块",3,"推荐品牌：西门子"]
[null,null,"16DI模块","321-1BH01","块",1,"推荐品牌：西门子"]
[null,null,"32DO模块","322-1BL00","块",1,"推荐品牌：西门子"]
[null,null,"8AI模块","331-7KF02","块",2,"推荐品牌：西门子"]
[null,null,"8AO模块","332-5HF00","块",1,"推荐品牌：西门子"]
[null,null,"中间继电器","DC24V 8脚","套",22,"推荐品牌：正泰"]
[null,null,"接触器","CJX-1210","台",22,"推荐品牌：正泰"]
[null,null,"过热继电器","型号根据电机功率再定","台",22,"推荐品牌：正泰"]
[null,null,"三档旋钮开关","三档","个",22,"推荐品牌：正泰"]
[null,null,"启+停按钮","AC220V 红+绿","个",44,"推荐品牌：正泰"]
[null,null,"接线端子","UK 4 EN","只",22]
[null,null,"接线端子","UK 2.5 EN","只",20]
[null,null,"2.5mm2主线","2.5mm2 黄、绿、红","批",1]
[null,null,"1mm2 控制线","1*1mm2","圈",8]
[null,null,"线槽","50*50  12m","m",1]
[null,null,"线号与标识","号码管+标识","批",1]
[null,null,"柜内辅助组件","号码管、地零排杂项","批",1]
[14,"电缆","柜体进线电缆","YJV - 3×16mm²+10mm²","M",5,"国标"]
[null,null,"动力电缆","YJV -3×4mm²+1x2.5","M",150,"国标"]
[null,null,"动力电缆","YJV -3×2.5mm²+1x1.5","M",250,"国标"]
[null,null,"信号线缆（每个仪表按30米/个估算）","ZRC-DJYVP-2*2*1.0","M",480,"国标"]
[null,null,"桥架（往调节池方向）","100×50","M",50]
[null,null,"桥架弯头","100×50","个",10]
[null,null,"波纹管","DN20 加厚型","M",30]
[null,null,"机具耗材","机具耗材","批",1]
[null,null,"安装、接线、调试",null,"工",28]
[null,"管材、配件","零星管材与配件","配套","项",1,"钢丝软管，螺栓，pvc阀门，抱箍，钢材，水泥等",null,null,"钢丝软管，螺栓，pvc阀门，抱箍，钢材，水泥等"]
["总价："]
["注：本次报价为包干价格。（包含设备税费、运输、配件、拆卸、安装及完成安装所需的准备工作、调试等完成该项目建设并满足运营要求的所有内容的总费用）"]

{"sheet":"化验室易耗品（自行采购）","index":1,"n_rows":33,"n_cols":8,"rows_kept":33,"flags":["formulas_cached_only"]}
[]
["布氏漏斗","布氏漏斗φ150",4,"个","唐山"]
["分液漏斗聚四氟乙烯活塞","F4梨形分液漏斗(聚四氟乙烯梨形分液漏斗)500ml",10,"个","蜀牛"]
["漏斗架","有机玻璃分液漏斗架500ml-4孔",2,"个","江苏"]
["中速定量滤纸12.5cm","定量滤纸φ12.5(中)",10,"个","富阳"]
["不锈钢托盘大号40*30cm","不锈钢方盘40-30",10,"盒","上海",null,null,"搪瓷"]
["5ML塑料吸管","一次性塑料滴管(一次性吸管)5ml-100支/包",1,"包","泰州"]
["玻璃棉","玻璃棉(玻璃纤维)500g",1,"包","金山"]
["医用橡胶手套（XS号或S号）","无医用",100,"双","高邦"]
["擦镜纸","擦镜纸(镜头纸)(100张)",20,"本","富阳"]
["瓷蒸发皿","陶瓷元皿(蒸发皿)150ml",40,"个","大明"]
["玻璃砂芯漏斗","玻砂漏斗(砂芯漏斗 玻砂滤斗)G3-40ml",20,"个","鹿头"]
["瓷坩埚","坩埚50ml",30,"个","大明"]
["刻度移液管1ml","刻度吸管1ml-A级",10,"支","北玻"]
["刻度移液管2ml","刻度吸管2ml-A级",10,"支","北玻"]
["刻度移液管10ml","刻度吸管10ml -A级",10,"支","北玻"]
["刻度移液管20ml","刻度吸管20ml-A级",5,"支","北玻"]
["硫代硫酸钠","硫代硫酸钠(大苏打)AR500g",1,"瓶","天正"]
["乙二胺四乙酸二钠","乙二胺四乙酸二钠(EDTA二钠)AR250g",1,"瓶","光复"]
["四氯乙烯","四氯乙烯(环保)IR500ml",1,"瓶","科密欧"]
["无水硫酸钠","无水硫酸钠AR500g",1,"瓶","福晨"]
["AR250g硅酸镁","硅酸镁(硅镁型吸附剂)60-100目 AR250g",1,"瓶","科密欧"]
["AR100m正十六烷","十六烷(正十六烷)AR100ml",1,"瓶","科密欧"]
["AR500ml异辛烷","异辛烷AR500ml",1,"瓶","天正"]
["AR500ml 苯","苯(安息油)AR500ml",1,"瓶","川东"]
["氯仿(三氯甲烷)","AR500g",1,"瓶","川东"]
["磷酸二氢纳","磷酸二氢钠AR500g",1,"瓶","科隆"]
["亚甲基蓝","亚甲基蓝(次甲基蓝 亚甲蓝)BS25g",1,"瓶","光复"]
["酚酞","酚酞Ind25g",1,"瓶","科隆"]
["葡萄糖（优级纯）","葡萄糖GR500g",1,"瓶","科密欧"]
["谷氨酸（优级纯）","L-谷氨酸(谷氨酸.麸氨酸.L(+)-谷氨酸.氨基戊二酸.L-2-氨基戊二酸.L-α-氨基戊二酸)AR25g",1,"瓶","科密欧"]
["直链烷基苯磺酸钠贮备液","直链烷基苯磺酸钠(十二烷基苯磺酸钠)50ml  0.1mg/ml",5,"支","坛墨"]
["石油类标准贮备液","石油类标准贮备液10000mg/10ml",5,"支","坛墨"]